**SECTION 262300 – POWER MONITORS FOR LOW VOLTAGE SWITCHGEAR**

|  |
| --- |
| **This section is a partial spec noting a Special Product Requirement for MAA. Designer shall complete the specification with information applicable to the project.**  |

**PART 2 - PRODUCTS**

* 1. COMPONENTS
1. Multifunction Digital-Metering Monitor: All double-ended substations shall be equipped with a multifunction digital-metering monitor located at each secondary main circuit breaker. Metering monitor shall be sole-sourced exclusively from Square-D. There will be "No Exceptions Allowed". Metering monitor shall have as a minimum all capabilities of Square-D CM3350 circuit monitor. Metering monitor display and control unit shall be flush or semi-flush mounted in instrument component door. Metering monitor shall be fully compatible with Johnson Controls N2 protocol for monitoring and displaying basic electrical data.